## Sheet1
|  | Column A | Column B | Column C | Column D | Column E
Item | Description | Quantity Each (A) | New Unit Price (B) | Subtotal (A * B) | Recertified Unit Price ( C) | Subtotal (A * C)
1 | 200 CLASS CFH (NTC) SCREWED CASE ALUMINUM GAS METERS WITH CONNECTIONS (General) | 2000 |  | 0 |  | 0
1) HUBS: SPRAGUE 1A
2) CAPACITY: 250 CFH OF .60 SG NATURAL GAS AT 1/2" W.C. DIFFERENTIAL
3) MAXIMUM WORKING PRESSURE: 5 PSIG
4) CONNECTIONS: 2 - INSUL 3/4" MALE PIPE THREAD GALV.
5) COMPATIBLE WITH ERT MODEL ERG-5006
2 | 400 CLASS CFH (NTC) ALUMINUM GAS METERS WITH CONNECTIONS | 300 |  | 0 |  | 0
1) HUBS: AMERICAN 425 - 45 LT.; INVENSYS 415 - 45 LT.: ACTARIS 400 - SPRAGUE STD.
2) CAPACITY: 400 CFH OF .60 SG NATURAL GAS AT 1/2" W.C. DIFFERENTIAL
3) MAXIMUM WORKING PRESSURE: 10 PSIG
4) CONNECTIONS: 2 - 1 1/2" INSULATED MALE SWIVELS
5) COMPATIBLE WITH ERT MODEL ERG-5006
3 | 600 CLASS CFH (NTC) ALUMINUM GAS METERS WITH CONNECTIONS | 300 |  | 0 |  | 0
1) HUBS: 45 LT.
2) CAPACITY: 630 CFH OF .60 SG NATURAL GAS AT 1/2" W.C. DIFFERENTIAL
3) MAXIMUM WORKING PRESSURE: 25 PSIG
4) CONNECTIONS: 2 - 1 1/2" INSULATED MALE SWIVELS
5) COMPATIBLE WITH ERT MODEL ERG-5006
4 | 600 CLASS CFH (NTC) ALUMINUM GAS METERS WITH CONNECTIONS (Can be used for right to left) | 25 |  | 0 |  | 0
1) HUBS: 45 LT.
2) CAPACITY: 630 CFH OF .60 SG NATURAL GAS AT 1/2" W.C. DIFFERENTIAL
3) MAXIMUM WORKING PRESSURE: 25 PSIG
4) CONNECTIONS: 2 - 1 1/2" INSULATED MALE SWIVELS
5) COMPATIBLE WITH ERT MODEL ERG-5006
5 | 800 CLASS CFH (NTC) ALUMINUM GAS METERS WITH CONNECTIONS | 40 |  | 0 |  | 0
1) HUBS: SPRAGUE STANDARD
2) CAPACITY: 1000 CFH OF .60 SG NATURAL GAS AT 1/2" W.C. DIFFERENTIAL
3) MAXIMUM WORKING PRESSURE: 25 PSIG
4) CONNECTIONS 2 - 2" FEMALE INSULATED FEMALE SWIVEL GALVANIZED
5) COMPATIBLE WITH ERT MODEL ERG-5006
6 | 800 CLASS CFH (NTC) ALUMINUM GAS METERS WITH CONNECTIONS (With 2lb dial) | 40 |  | 0 |  | 0
1) HUBS: SPRAGUE STANDARD
2) CAPACITY: 1000 CFH OF .60 SG NATURAL GAS AT 1/2" W.C. DIFFERENTIAL
3) MAXIMUM WORKING PRESSURE: 25 PSIG
4) CONNECTIONS 2 - 2" FEMALE INSULATED FEMALE SWIVEL GALVANIZED
5) COMPATIBLE WITH ERT MODEL ERG-5006
7 | 1000 CLASS CFH (NTC) ALUMINUM GAS METERS WITH CONNECTIONS (With 2 lb Dial) | 40 |  | 0 |  | 0
1) HUBS: SPRAGUE STANDARD
2) CAPACITY: 1000 CFH OF .60 SG NATURAL GAS AT 1/2" W.C. DIFFERENTIAL
3) MAXIMUM WORKING PRESSURE: 25 PSIG
4) CONNECTIONS 2 - 2" FEMALE INSULATED FEMALE SWIVEL GALVANIZED
5) COMPATIBLE WITH ERT MODEL ERG-5006
8 | 1000 CLASS CFH (NTC) ALUMINUM GAS METERS WITH CONNECTIONS (With 2 lb Dial) Right to left | 40 |  | 0 |  | 0
1) HUBS: SPRAGUE STANDARD
2) CAPACITY: 1000 CFH OF .60 SG NATURAL GAS AT 1/2" W.C. DIFFERENTIAL
3) MAXIMUM WORKING PRESSURE: 25 PSIG
4) CONNECTIONS 2 - 2" FEMALE INSULATED FEMALE SWIVEL GALVANIZED
5) COMPATIBLE WITH ERT MODEL ERG-5006
9 | 1000 CLASS CFH (NTC) ALUMINUM GAS METERS WITH CONNECTIONS (With 7 inch Dial) | 40 |  | 0 |  | 0
1) HUBS: SPRAGUE STANDARD
2) CAPACITY: 1000 CFH OF .60 SG NATURAL GAS AT 1/2" W.C. DIFFERENTIAL
3) MAXIMUM WORKING PRESSURE: 25 PSIG
4) CONNECTIONS 2 - 2" FEMALE INSULATED FEMALE SWIVEL GALVANIZED
5) COMPATIBLE WITH ERT MODEL ERG-5006
10 | 1000 CLASS CFH (NTC) ALUMINUM GAS METERS WITH CONNECTIONS (With 7 inch Dial) Right to Left | 20 |  | 0 |  | 0
1) HUBS: SPRAGUE STANDARD
2) CAPACITY: 1000 CFH OF .60 SG NATURAL GAS AT 1/2" W.C. DIFFERENTIAL
3) MAXIMUM WORKING PRESSURE: 25 PSIG
4) CONNECTIONS 2 - 2" FEMALE INSULATED FEMALE SWIVEL GALVANIZED
5) COMPATIBLE WITH ERT MODEL ERG-5006
11 | ROMET OR ROOTS 3M ROTARY METER OR EQUIVALENT | 50 |  | 0 |  | 0
1) Base Rate (Q.Max) : 3000 acfh
2) Rangeability (+/-1%): 76:1 ratio
3) Rangeability (+/- 2%): 139:1 ratio
4) Start Rate: 2.1 cfh
5) Stop Rate 1.8 cfh
6) Flow Rate @ 0.5" W.C. Gas: 2580 cfh
7) Avg. Differential, 100% Flow: 1.05 in w.c.
8) Max. Operating Speed: 2000 rpm
9) Gear Ratio: 400:1 ratio
10) Displaced Volume/ Revolution: 0.025 cf
11) Drive Rate, CD: 10 cf/rev
12) Drive Rate, TD: 100 cf/rev
13) Odometer Turnover: 3.8 yrs.
14) Nominal Pipe Size: 2 in.
15) Flange-to-Flange: 6-3/4 in.
16) Bolts per Flange: 4
17) Flange Bolt Hole Depth 15/16 in.
18) Restricting Orfice (120%): 17/32 in.
12 | ROMET OR ROOTS 5M ROTARY METER OR EQUIVALENT | 30 |  | 0 |  | 0
1) Base Rate (Q.Max) : 5000 acfh
2) Rangeability (+/-1%): 120:1 ratio
3) Rangeability (+/- 2%): 215:1 ratio
4) Start Rate: 1.2 cfh
5) Stop Rate 0.8 cfh
6) Flow Rate @ 0.5" W.C. Gas: 3975 cfh
7) Avg. Differential, 100% Flow: 1.05 in. w.c.
8) Max. Operating Speed: 2250 rpm
9) Gear Ratio: 270:1 ratio
10) Displaced Volume/ Revolution: 0.037037 cf
11) Drive Rate, CD: 10 cf/rev
12) Drive Rate, TD: 100 cf/rev
13) Odometer Turnover: 2.28 yrs.
14) Nominal Pipe Size: 3 in.
15) Flange-to-Flange: 6-3/4 in.
16) Bolts per Flange: 4
17) Flange Bolt Hole Depth 15/16 in.
18) Restricting Orfice (120%): 23/32 in.
13 | ROMET OR ROOTS 7M ROTARY METER OR EQUIVALENT | 10 |  | 0 |  | 0
1) Base Rate (Q.Max) : 7000 acfh
2) Rangeability (+/-1%): 67:1 ratio
3) Rangeability (+/- 2%): 115:1 ratio
4) Start Rate: 5.33 cfh
5) Stop Rate 3.39 cfh
6) Flow Rate @ 0.5" W.C. Gas: 5400 cfh
7) Avg. Differential, 100% Flow: 1.6 in. w.c.
8) Max. Operating Speed: 1867 rpm
9) Gear Ratio: 160:1 ratio
10) Displaced Volume/ Revolution: 0.0325 cf
11) Drive Rate, CD: 10 cf/rev
12) Drive Rate, TD: 100 cf/rev
13) Odometer Turnover: 1.63 yrs.
14) Nominal Pipe Size: 3 in.
15) Flange-to-Flange: 9-1/2 in.
16) Bolts per Flange: 4
17) Flange Bolt Hole Depth 15/16 in.
18) Restricting Orfice (120%): 13/16 in.
14 | ROMET OR ROOTS 11M ROTARY METER OR EQUIVALENT | 10 |  | 0 |  | 0
1) Base Rate (Q.Max) : 11000 acfh
2) Rangeability (+/-1%): 124:1 ratio
3) Rangeability (+/- 2%): 227:1ratio
4) Start Rate: 3.88 cfh
5) Stop Rate 3.23 cfh
6) Flow Rate @ 0.5" W.C. Gas: 7300 cfh
7) Avg. Differential, 100% Flow: 1.6 in. w.c.
8) Max. Operating Speed: 1833 rpm
9) Gear Ratio: 100:1 ratio
10) Displaced Volume/ Revolution: 0.1 cf
11) Drive Rate, CD: 10 cf/rev
12) Drive Rate, TD: 100 cf/rev
13) Odometer Turnover: 1.04 yrs.
14) Nominal Pipe Size: 4 in.
15) Flange-to-Flange: 9-1/2 in.
16) Bolts per Flange: 8
17) Flange Bolt Hole Depth 1-1/16 in.
18) Restricting Orfice (120%): 1 in.
15 | HSR 3/4" ANGLE BODY | 1500 |  | 0 |  | 0
1) INLET PRESSURE: 60 PSIG
2) OUTLET PRESSURE: 7" W.C. TO 2LB W.C.
3) ORIFICE SIZE: 1/8"
4) VENT POSITION: SENSUS - #14; FISHER - E; ACTARIS - #13; LANCASTER - 9-9;
AMERICAN - VALVE HEAD (A) VENT #1
16 | HSR 3/4" ANGLE BODY | 500 |  | 0 |  | 0
1) INLET PRESSURE: 6 PSIG
2) OUTLET PRESSURE: 7" W.C. TO 2LB W.C.
3) ORIFICE SIZE: 3/8"
4) VENT POSITION: SENSUS - #14; FISHER - E; ACTARIS - #13; LANCASTER - 9-9;
AMERICAN - VALVE HEAD (A) VENT #1
17 | HSR 3/4" GLOBE BODY | 200 |  | 0 |  | 0
1) INLET PRESSURE: 60 PSIG
2) OUTLET PRESSURE: 7" W.C. TO 2LB W.C.
3) ORIFICE SIZE: 1/8"
4) VENT POSITION: SENSUS - #14; FISHER - E; ACTARIS - #13; LANCASTER - 9-9;
AMERICAN - VALVE HEAD (A) VENT #1
18 | HSR 3/4" GLOBE BODY | 200 |  | 0 |  | 0
1) INLET PRESSURE: 6 PSIG
2) OUTLET PRESSURE: 7" W.C. TO 2LB W.C.
3) ORIFICE SIZE: 3/8"
4) VENT POSITION: SENSUS - #14; FISHER - E; ACTARIS - #13; LANCASTER - 9-9;
AMERICAN - VALVE HEAD (A) VENT #1
19 | HSR 1" GLOBE BODY | 300 |  | 0 |  | 0
1) INLET PRESSURE: 60 PSIG
2) OUTLET PRESSURE: 7" W.C. TO 2LB W.C.
3) ORIFICE SIZE: 1/8"
4) VENT POSITION: SENSUS - 105; FISHER - 3F; ACTARIS - #5; LANCASTER - 6-6;
AMERICAN - VALVE HEAD (C) VENT #2
20 | HSR 1" GLOBE BODY | 300 |  | 0 |  | 0
1) INLET PRESSURE: 6 PSIG
2) OUTLET PRESSURE: 7" W.C. TO 2LB W.C.
3) ORIFICE SIZE: 3/8"
4) VENT POSITION: SENSUS - 105; FISHER - 3F; ACTARIS - #5; LANCASTER - 6-6;
AMERICAN - VALVE HEAD C VENT #2
21 | DIRECT OPERATED PRESSURE REDUCING REGULATOR (EQUIVALENT TO FISHER 627) | 15 |  | 0 |  | 0
1) LARGE RESIDENTIAL 10 LB OR HIGHER
2) INLET PRESSURE: 60 PSIG
3) OUTLET PRESSURE: 5-20 PSIG
4) ORIFICE SIZE: 1/4"
5) 1" BODY
6) INTERNAL RELIEF WITHOPEN THROAT
CAPACITY FULL RELIEF
60# INLET
10# OUT
1/4"ORIFICE 4710SCFH
22 | CONSTANT PRESSURE PILOT LOADED REGULATOR LT GREEN MAIN SPRING, BLUE PILOT SRING (EQUIVALENT TO CL231) | 25 |  | 0 |  | 0
1) INLET PRESSURE: 60 PSIG
2) OUTLET PRESSURE: 1LB-20LB
3) ORIFICE SIZE: 3/8" with ability to interchange
4) 2" BODY
5)INTERNAL BLEED TO PREVENT VAPOR-LOCK UP
6) VENT POSITION: SENSUS - 105; FISHER - 3F; ACTARIS - #5; LANCASTER - 6-6;
AMERICAN - VALVE HEAD C VENT #2
CAPACITY TOKEN RELIEF
60# INLET 1-20#OUTLET
1/4" ORIFICE 3/8"ORIFICE
4600 SCFH 7500SCFH
23 | 2" FLANGED SPRING LOADED, SELF REGULATED GAS REGULATOR WITH INTERNAL RELIEF VALVE (EQUIVALENT TO ITRON B34) | 30 |  | 0 |  | 0
1) INLET PRESSURE: 60 PSIG .60 SG NATURAL GAS
2) OUTLET PRESSURE: 7" W.C. TO 14" W.C.
(MUST BE CAPABLE OF OUTLET PRESSURE UP TO 2 PSI WITH ONLY A CHANGE OF SPRING)
3) BRASS ORIFICE SIZE: 3/8", WITH THE ABILITY TO INTERCHANGE ORFICES
5) ADJUSTABLE LOADING RING
6) 1 IN. INTERNAL RELIEF VALVE FULL RELIEF
7) CONTROLLED SIZE BREATHER ORFICE
8) VENT POSITION: SENSUS -105; FISHER - 3F; ACTARIS - #5; LANCASTER - 6-6;
CAPACITY:
60# IN 60# IN 5#IN 5#IN
7"OUT 2# OUT 7"OUT 2# OUT
1/4"ORIFICE 1/4"ORIFICE 3/8 X 1/2ORIFICE 3/8 X 1/2ORIFICE
4500SCFH 4000SCFH 2400SCFH 1500SCFH
24 | 2" FEMALE PIPE THREAD SPRING LOADED, SELF OPERATED GAS REGULATOR WITH INTERNAL RELIEF VALVE (EQUIVALENT TO ITRON B34) | 30 |  | 0 |  | 0
1) INLET PRESSURE: 60 PSIG .60 SG NATURAL GAS
2) OUTLET PRESSURE: 7" W.C. TO 14" W.C.
(MUST BE CAPABLE OF OUTLET PRESSURE UP TO 2 PSI WITH ONLY A CHANGE OF SPRING)
3) BRASS ORIFICE SIZE: 3/8", WITH THE ABILITY TO INTERCHANGE ORFICES
5) ADJUSTABLE LOADING RING
6) 1 IN. INTERNAL RELIEF VALVE FULL RELIEF
7) CONTROLLED SIZE BREATHER ORFICE
8) VENT POSITION: SENSUS -105; FISHER - 3F; ACTARIS - #5; LANCASTER - 6-6;
CAPACITY:
60# IN 60# IN 5#IN 5#IN
7"OUT 2# OUT 7"OUT 2# OUT
1/4"ORIFICE 1/4"ORIFICE 3/8 X 1/2ORIFICE 3/8 X 1/2ORIFICE
4500SCFH 4000SCFH 2400SCFH 1500SCFH
25 | 1 1/4" SPRING LOADED, SELF OPERATED GAS REGULATOR WITH INTERNAL RELIEF (EQUIVALENT TO B34SR) | 10 |  | 0 |  | 0
1) INLET PRESSURE: 60 PSIG .60 SG NATURAL GAS
2) OUTLET PRESSURE: 7" W.C. TO 14" W.C.
(MUST BE CAPABLE OF OUTLET PRESSURE UP TO 2 PSI WITH ONLY A CHANGE OF SPRING)
3) BRASS ORIFICE SIZE: 3/8" X 1/2" with the ability to interchange orifice
5) ADJUSTABLE LOADING RING
6) 1 IN. INTERNAL RELIEF VALVE FULL RELIEF
7) CONTROLLED SIZE BREATHER ORFICE
8) VENT POSITION: SENSUS -105; FISHER - 3F; ACTARIS - #5; LANCASTER - 6-6;
CAPACITY:
60# IN 60# IN 5#IN 5#IN
7"OUT 2# OUT 7"OUT 2# OUT
1/4" x 3/8" ORIFICE 3/8 X 1/2ORIFICE 3/8 X 1/2ORIFICE 7/8" X 1"ORIFICE
4080SCFH 3550SCFH 1960SCFH 1170SCFH
26 | 1 1/4" SPRING LOADED, SELF OPERATED GAS REGULATOR WITH INTERNAL RELIEF (EQUIVALENT TO B34SR) | 10 |  | 0 |  | 0
1) INLET PRESSURE: 60 PSIG .60 SG NATURAL GAS
2) OUTLET PRESSURE: 7" W.C. TO 14" W.C.
(MUST BE CAPABLE OF OUTLET PRESSURE UP TO 2 PSI WITH ONLY A CHANGE OF SPRING)
3) BRASS ORIFICE SIZE: 7/8" X 1"
5) ADJUSTABLE LOADING RING
6) 1 IN. INTERNAL RELIEF VALVE FULL RELIEF
7) CONTROLLED SIZE BREATHER ORFICE
8) VENT POSITION: SENSUS -105; FISHER - 3F; ACTARIS - #5; LANCASTER - 6-6;
CAPACITY:
60# IN 60# IN 5#IN 5#IN
7"OUT 2# OUT 7"OUT 2# OUT
1/4" x 3/8" ORIFICE 3/8 X 1/2ORIFICE 3/8 X 1/2ORIFICE 7/8" X 1"ORIFICE
4080SCFH 3550SCFH 1960SCFH 1170SCFH
27 | SPRING LOADED THROTTLING RELIEF BACK PRESSURE REGULATOR (OVERPRESSURE RELIEF REGULATOR) (EQUIVALENT TO FISHER 289) | 25 |  | 0 |  | 0
1) 1 INCH BODY
2) 15#-50# INTEGRAL
28 | SPRING LOADED THROTTLING RELIEF BACK PRESSURE REGULATOR (OVERPRESSURE RELIEF REGULATOR) (EQUIVALENT TO FISHER 289) | 25 |  | 0 |  | 0
1) 1 INCH BODY
2) 4LB-15LB INTEGRAL
29 | PILOT OPERATED PRESSURE REDUCING REGULATOR (EQUIVALENT TO FISHER 99) | 5 |  | 0 |  | 0
Distribution, Industrial, and Commercial applications
1) Inlet: Up to 175 psig/12.1 bar
2) Outlet: 1-20# (Large commercial and reg, stations)
3) Integral Token Relief (designed to relieve overpressure caused by thermal expansion
4) Orifice: 1/2"
30 | PRESSURE REDUCING REGULATOR FOR REGULATOR STATIONS AND DISTRIC GATE STATIONS (EQUIVALENT TO FISHER 299) | 5 |  | 0 |  | 0
1) Inlet: Up to 1000 psig/69.1 bar
2) Outlet: 2" W.C.to 100 psig
3)Brass Seat
4)Orifice: 7/8"
5) Internal pressure registration
6) 2 inch flanged body
31 | STRAINERS | 50 |  | 0 |  | 0
1) 2" Threaded body
2) 100 mesh
32 | FILTER 2" (DRY PARTICLE) | 10 |  | 0 |  | 0
1) 2" Flanged body
2) 180 psig max
3) 10 micron filter
33 | FILTER 3" (DRY PARTICLE) | 2 |  | 0 |  | 0
1) 3" Flanged body
2) 180 psig max
3) 10 micron filter
34 | FILTER 4" (DRY PARTICLE) | 2 |  | 0 |  | 0
1) 4" Flanged body
2) 180 psig max
3) 10 micron filter
| GRAND TOTALS: |  |  | Total for New Units (Total of Column C) |  | Total for Recertified Units (Total of Column E)
|  |  |  | 0 |  | 0